## Cover Page
|  | Zishan Engineers (Pvt.) Ltd. An ISO 9001-2015 certified company, 47/F, Block 6, PECHS, Karachi-Pakistan Tel: (92-21) 34393045-48 & 34310151-54 Fax: (92-21) 34533430 & 34310156 E-mail : contact@zishanengineers.com, Web : www.zishanengineers.com |  | Document No. | 165-2-BQM-001
|  |  |  | Revision | 1
|  |  |  | Date | 04-07-2018
|  |  |  | Total Pages (inc front cover) | 7
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BOQ/BID PRICE SCHEDULE FOR SUPPLY & INSTALLATION OF MECHANICAL / FIRE FIGHTING / COMPANY SUPPLIED EQUIPMENT & PACKAGES
1 | 2018-07-04 | Re-Issued for Tender | MAS | MIAH | SH
0 | 2018-06-04 | Issued for Tender | MAS | MIAH | SH
Rev. | Date | Description | Prepared By | Checked By | Approved By

## Sheet1
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BOQ/BID PRICE SCHEDULE FOR SUPPLY & INSTALLATION OF MECHANICAL / FIRE FIGHTING / COMPANY SUPPLIED EQUIPMENT & PACKAGES
ITEM | D E S C R I P T I O N | QTY. | UNIT | Supply | [5 empty] | Services |  |  |  | Total Amount (Supply + Services) (Pak. Rs.) | R E M A R K S
|  |  |  | Unit Rate (Pak Rs.) | Total Supply (Pak Rs.) | GST on Supply items (Pak. Rs.) | Total Supply inclusive of GST | Third Party Pre Shipment Inspection (Pak. Rs.) | Total Supply inclusive of GST & Pre-Shipment Inspection | Unit Rate (Pak Rs.) | Total Services (Pak Rs.) | GST & Provincial tax on Services (Pak.Rs.) | Total Services inclusive of GST & Provincial Tax on Services (Pak.Rs.)
[5 empty] | A | B | C = A+B | D | E = C+D |  | F | G | H = F+G | I=E+H
1 | INSTRUMENT AIR PACKAGE
1.1 | SUPPLY OF MATERIAL, FABRICATION, INSTALLATION, ERECTION, TESTING AND COMMISSIONING OF INSTRUMENT AIR RECEIVER VESSEL (3000-V330B) AS PER REFERENCE DOCUMENTS AND APPLICABLE STANDARDS COMPLETE IN ALL RESPECT. REFERENCE DOCUMENTS : 165-2-DSM-114 165-2-MPV-101 | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | WEIGHTS GIVEN ARE APPROXIMATE AND FOR BIDDING PURPOSE ONLY. FINAL WEIGHTS WILL BE PROVIDED WITH "ISSUED FOR CONSTRUCTION" DRAWINGS TO THE SUCCESSFUL BIDDER
1.2 | INSTALLATION, TESTING, CLEANING AND COMMISSIONING OF INSTRUMENT AIR PACKAGE IN ACCORDANCE WITH DRAWINGS, SPECIFICATIONS, RELEVANT STANDARDS AND AS DIRECTED BY OWNER'S REPRESENTATIVE, COMPLETE IN ALL RESPECT. REFERENCE DOCUMENTS : 165-2-PID-107 SEE VENDOR'S DATA FOR INSTRUMENT AIR SYSTEM IN SUPPLEMENTARY TECHNICAL DOCS OF SECTION-V OF TENDER DOCS. | 1 | L.S |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | INSTRUMENT AIR SYSTEM IS FREE ISSUED ITEM EXCEPT 3000-V330B INSTRUMENT AIR RECEIVER VESSEL WHICH IS IN CONTRACTOR'S SCOPE AND INSTALLATION OF COMPLETE INSTRUMENT AIR PACKAGE IS CONTRACTOR'S RESPONSIBILITY.
2 | GAS ENGINE DRIVEN RECIPROCATING COMPRESSOR PACKAGE
2.1 | INSTALLATION, TESTING AND COMMISSIONING ASSISTANCE OF COMPRESSORS AS PER THE DOCUMENTS REFERENCE DOCUMENTS : SEE VENDOR'S DATA FOR GAS ENGINE DRIVEN RECIPROCATING COMPRESSOR PACKAGE IN SUPPLEMENTARY TECHNICAL DOCS OF SECTION-V OF TENDER DOCS. | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3 | TANKAGE
3.1 | FIRE WATER TANK T-3501
| SUPPLY OF MATERIAL, FABRICATION, WELDING, INSTALLATION, TESTING, CLEANING, BOX-UP AND COMMISSIONING OF 1 NO. 12.190 m DIA. X 13.000 m Height FIRE WATER TANK (T-3501), IN ACCORDANCE WITH DRAWINGS, SPECIFICATIONS, RELEVANT STANDARDS AND AS DIRECTED BY OWNER'S REPRESENTATIVE, COMPLETE IN ALL RESPECT. THE WORKS INCLUDE THE FOLLOWING: REFERENCE DOCUMENTS : 165-2-PID-109 (SHEET 2 OF 4) 165-2-MST-3501 165-2-DSM-110 | [13 empty] | THE RATES OF ITEM B (ALL PARTS), F (ALL PARTS) & D IN S.NO. 1.1.1 SHALL BE INCLUSIVE OF SURFACE PREPARATION & PAINTING AS PER PAINTING SPECIFICATION. WEIGHTS GIVEN ARE APPROXIMATE AND FOR BIDDING PURPOSE ONLY. FINAL WEIGHTS WILL BE PROVIDED WITH "ISSUED FOR CONSTRUCTION" DRAWINGS TO THE SUCCESSFUL BIDDER
a) | ROOF PLATES | 6731 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | ROOF STRUCTURE | 4271 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
c) | SHELL PLATES | 27823 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
d) | CURB ANGLE | 349 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
e) | BOTTOM PLATES | 10327 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
f) | TANK NOZZLES AND APPURTENANCES INCLUDING THE FOLLOWING: | 3207 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
i) | SHELL AND ROOF MANHOLES
ii) | SHELL AND ROOF NOZZLES
iii) | PRODUCT DRAW-OFF WITH INTERNAL PIPES & NAME PLATE
g) | SPIRAL STAIRCASE AND HAND RAIL | 1692 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
| SUB TOTAL FOR T-3501 | 54400 | KG
3.2 | DIESEL DAY TANK (T-4001)
| SUPPLY OF MATERIAL, FABRICATION, WELDING, INSTALLATION, TESTING, CLEANING, BOX-UP AND COMMISSIONING OF 1 NO. 2.788 m LENGTH x 1.738 m WIDTH x 1.834 m HEIGHT DIESEL DAY TANK (T-4001) , IN ACCORDANCE WITH DRAWINGS, SPECIFICATIONS, RELEVANT STANDARDS AND AS DIRECTED BY OWNER'S REPRESENTATIVE, COMPLETE IN ALL RESPECT. THE WORKS INCLUDE THE FOLLOWING: REFERENCE DOCUMENTS : 165-2-PID-108 165-2-MST-4001 165-2-DSM-113 | [13 empty] | THE RATES OF ITEMS STIFFENER, LADDER PLATFORM MATERIAL, NOZZLES & APPURTENANCES (all parts) , CURB ANGLE SHALL BE INCLUSIVE OF SURFACE PREPARATION & PAINTING AS PER PAINTING SPECIFICATION. WEIGHTS GIVEN ARE APPROXIMATE AND FOR BIDDING PURPOSE ONLY. FINAL WEIGHTS WILL BE PROVIDED WITH "ISSUED FOR CONSTRUCTION" DRAWINGS TO THE SUCCESSFUL BIDDER
a) | ROOF PLATES | 484 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | SHELL PLATES | 1574 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
c) | CURB ANGLE | 102 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
d) | BOTTOM PLATES | 533 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
e) | STIFFENER ANGLE | 409 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
f) | SUPPORTED BEAM | 195 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
g) | TANK NOZZLES AND APPURTENANCES INCLUDING THE FOLLOWING: | 279 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
i) | SHELL AND ROOF MANHOLES
ii) | SHELL AND ROOF NOZZLES
iii) | PRODUCT DRAW-OFF WITH INTERNAL PIPES
iv) | NAME PLATE
h) | LADDER,PLATFORM AND HAND RAIL | 74 | KG. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
| SUB TOTAL FOR T-4001 | 3650 | KG
3.3 | SUPPLY OF ALL MATERIALS, INSTALLATION AND TESTING OF FLOAT TYPE LEVEL INDICATOR FOR FOLLOWING TANKS, COMPLETE IN ALL RESPECTS AS PER RELEVANT DOCUMENT: REFERENCE DOCUMENTS : 165-2-DSI-005
a) | 12.190 m DIA. x 13.000 m HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 2.788 M LENGTH X 1.738 M WIDTH x 1.834 M HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.4 | VACUUM BOX TESTING OF BOTTOM FOR THE FOLLOWING TANKS: | [13 empty] | CONTRACTOR TO SUBMIT PROCEDURE FOR APPROVAL FROM OWNER.
a) | 12.190 m DIA. x 13.000 m HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 2.788 M LENGTH X 1.738 M WIDTH x 1.834 M HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.5 | HYDROSTATIC TESTING OF FOLLOWING TANKS: | [13 empty] | ARRANGEMENT OF WATER FOR HYDROSTATIC TESTING OF TANK IS CONTRACTOR'S RESPONSIBILITY.
a) | 12.190 m DIA. x 13.000 m HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 2.788 M LENGTH X 1.738 M WIDTH x 1.834 M HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.6 | CALIBRATION OF FOLLOWING TANKS : (USING OPTICAL LINE METHOD). (WITH APPROVAL FROM PWD) | [13 empty] | CONTRACTOR TO SUBMIT PROCEDURE FOR APPROVAL FROM THE OWNER. CONTRACTOR SHALL BE RESPONSIBLE FOR GETTING NECESSARY APPROVALS FROM PWD AND RELEVANT DEPARTMENTS. CALIBRATION SHALL BE PERFORMED BY REPUTABLE THIRD PARTY AGENCY PREFERABLY SGS. ANY OTHER AGENCY NOMINATED FOR CALLIBRATION SHALL FIRST BE APPROVED FROM OWNER. CHARGES OF THIRD PARTY AGENCY SHALL BE AT CONTRACTOR'S EXPENSE
a) | 12.190 m DIA. x 13.000 m HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 2.788 M LENGTH X 1.738 M WIDTH x 1.834 M HEIGHT | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.7 | SUPPLY OF ALL MATERIALS, SURFACE PREPARATION BY SAND BLASTING TO S.A. 2 1/2 AND PAINTING OF TANKS WHICH INCLUDES 2 COATS OF RED OXIDE (LEAD FREE) PRIMER (40-45 MICRONS EACH) FOLLOWED BY TWO COATS OF ALKYD ENAMEL (20-25 MICRONS EACH) GIVING A TOTAL DRY FILM THICKNESS (DFT) OF 125 MICRONS MINIMUM ON EXTERNAL SURFACES (INCLUDING ALL NOZZLES ETC.) OF THE FOLLOWING TANK ACCORDING TO SPECIFICATIONS AND TO THE ENTIRE SATISFACTION OF THE OWNER'S REPRESENTATIVE. | [13 empty] | FOR DETAIL SEE SPECIFICATION 165-2-SPM-013
a) | 12.190 m DIA. x 13.000 m HEIGHT (1 NO.S) | 650 | SQ.M |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 2.788 M LENGTH X 1.738 M WIDTH x 1.834 M HEIGHT (1 Nos.) | 32 | SQ.M |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.8 | SUPPLY OF ALL MATERIALS, SURFACE PREPARATION BY SAND BLASTING TO S.A. 2 1/2 AND APPLICATION OF 3 COATS OF COALTAR EPOXY (125 MICRONS EACH) GIVING A TOTAL DRY FILM THICKNESS OF 375 MICRONS. ON UNDER SIDE OF BOTTOM PLATES AND INTERNAL PAINTING ON INSIDE OF TANK SHELL HEIGHT FOR THE FIRE WATER TANK. | [13 empty] | FOR DETAIL SEE SPECIFICATION 165-2-SPM-013
a) | 12.190 m DIA. x 13.000 m HEIGHT (1 NO.S) | 175 | SQ.M |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.9 | SUPPLY OF ALL MATERIALS, SURFACE PREPARATION BY SAND BLASTING TO S.A. 2 1/2 AND APPLICATION OF 3 COATS OF EPOXY ULTRABUILD LINER (125 MICRONS EACH) GIVING A TOTAL DRY FILM THICKNESS OF 375 MICRONS. ON UNDER SIDE OF BOTTOM PLATES AND INTERNAL PAINTING ON 1 METER OF SHELL HEIGHT FOR THE FOLLOWING TANK
a) | 2.788 M LENGTH X 1.738 M WIDTH x 1.834 M HEIGHT (1 Nos.) | 25 | SQ.M |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4 | FIREWATER & FIREFIGHTING SYSTEM
THE SUPPLIED FIRE WATER EQUIPMENT SHALL COMPLY WITH THE FOLLOWING DOCUMENTS ATTACHED. ANY DEVIATION SHALL BE CLEARLY HIGHLIGHTED & JUSTIFIED BY THE SUPPLIER.
REFERENCE DRAWING NO.S:
165-2-PID-109 (FIRE WATER SYSTEM)
165-2-MPD-001 (TYPICAL DETAILS OF FIRE HYDRANT AND MONITOR)
REFERENCE DATA SHEETS & SPECIFICATIONS
165-2-SPM-035 (SPECIFICATION FOR FIRE FIGHTING SYSTEM).
165-2-SPM-041 (SPECIFICATION FOR MOBILE FOAM UNITS).
165-2-DSM-111 (DATA SHEET FOR FIRE HYDRANTS).
165-2-DSM-112 (DATA SHEET FOR FIRE MONITORS).
4.1 | FIRE WATER HYDRANTS:
| SUPPLY & INSTALLATION, ERECTION, TESTING AND COMMISSIONING OF FIREWATER HYDRANTS AS PER DATA SHEET NO. 165-2-DSM-111. | 12 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.2 | FIRE FOAM MONITORS:
| SUPPLY & INSTALLATION, ERECTION, TESTING AND COMMISSIONING OF FIRE FOAM MONITORS AS PER DATA SHEET NO. 165-2-DSM-112. | 13 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.3 | MOBILE FOAM UNITS:
| SUPPLY & INSTALLATION, ERECTION, TESTING, PLACEMENT AND COMMISSIONING OF TROLLEY MOUNTED MOBILE FOAM UNITS AS PER SPECIFICATION 165-2-SPM-041. | 8 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.4 | FIXED FOAM UNITS FOR STORAGE TANKS:
| SUPPLY & INSTALLATION OF SKID BASED FIXED FOAM UNITS WITH BLADDER TANK, PROPORTIONATER, PIPING, INSTRUMENTATION ETC. COMPLETE IN ALL RESPECTS. | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.5 | FOAM POURER / CHAMBER FOR TANKS:
| SUPPLY & INSTALLATION OF 4" 150#, RF FOAM POURER ASSEMBLY AND NOZZLE AND PIPING CLEATS AND ALL REQUIRED TESTING AS PER API-653 FOR FOLLOWING TANKS, IN ACCORDANCE WITH RELEVANT STANDARDS AND AS DIRECTED BY OWNER'S REPRESENTATIVE, COMPLETE IN ALL RESPECTS AS PER SITE CONDITION REFERENCE DOCUMENT: 165-2-DSM-115 165-2-MST-003 165-2-MST-004 | [13 empty] | CONTRACTOR TO SUBMIT PROCEDURE FOR INSTALLATION & TESTING FOR APPROVAL FROM OWNER ALONGWITH THE BID DOCUMENTS.
a) | 13.716 m DIA. x 9.010 m HEIGHT | 6 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 18.288 m DIA x 12.192 m HEIGHT | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.6 | COOLING WATER SPRAY SYSTEM FOR TANKS:
| SUPPLY & INSTALLATION OF COOLING WATER SPRAY SYSTEM & ALL REQUIRED TESTING AS PER API-653 FOR FOLLOWING TANKS, IN ACCORDANCE WITH RELEVANT STANDARDS AND AS DIRECTED BY OWNER'S REPRESENTATIVE, COMPLETE IN ALL RESPECTS AS PER SITE CONDITION REFERENCE DOCUMENT: 165-2-MST-001 165-2-MST-002 | [13 empty] | CONTRACTOR TO SUBMIT PROCEDURE FOR INSTALLATION & TESTING FOR APPROVAL FROM OWNER ALONGWITH THE BID DOCUMENTS.
a) | 13.716 m DIA. x 9.010 m HEIGHT | 6 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 18.288 m DIA x 12.192 m HEIGHT | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.7 | HOSE CABINET:
| SUPPLY & INSTALLATION OF FIRE HOSE CABINETS, FLOOR STANDING TYPE, MIN. 4' x 4' x 10' , FABRICATED FROM 16 SWG SHEET, CAPABLE OF HOLDING: | 8 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
a) | 2 NOS. HOSE REELS 2-1/2" ND x 30M LONG.
b) | 1NO. FOAM MAKING BRANCH WITH PICK-UP TUBE
c) | 1NO. TRIPLE PURPOSE NOZZLE.
4.8 | HOSE REEL:
| SUPPLY & INSTALLATION OF FIRE HOSE REELS OF 2-1/2" ND x 30 M LONG, WITH EXPANSION RING TYPE COUPLING MALE AND FEMALE TYPE ON EACH END RESPECTIVELY. HOSE TO BE NEOPRENE LINED AND COVERED WITH AN OIL ABRASIVE RESISTANT NEOPRANE OR PLASTIC COATING, HOSE SHALL BE SUITABLE FOR 200 PSIG PRESSURE. | 16 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.9 | BRANCH PIPE:
| SUPPLY & INSTALLATION, PLACEMENT OF SELF INDUCTING FOAM MAKING BRANCH PIPE RATED AT 50GPM AT 7 BARG HYDRANT PRESSURE WITH A THROW OF 40M SUITABLE FOR CONNECTION WITH 2-1/2" DIA. QUICK/INSTANEOUS TYPE COUPLING. | 8 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.1 | TRIPLE PURPOSE NOZZLE:
| SUPPLY & INSTALLATION OF TRIPLE PURPOSE NOZZLE FOR JET SPRAY AND FOG, RATED AT 80M3/HR. AT 7 BARG AND THROW OF 40M, SUITABLE FOR 2-1/2" DIA. QUICK/INSTANEOUS TYPE COUPLING. | 8 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.11 | FIRE EXTINGUISHERS
4.11.1 | SUPPLY & INSTALLATION AND PLACEMENT OF PORTABLE FIRE EXTINGUISHERS ABC, DRY CHEMICAL, NIPPON PAN-20 SD OR EQUIVALENT, POWDER TYPE COMPLETE WITH ALL ACCESSORIES & INITIAL CHARGE IN FOLLOWING CAPACITIES:
| 6 Kg. | 5 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.11.2 | SUPPLY & NSTALLATION AND PLACEMENT OF PORTABLE FIRE EXTINGUISHERS, CO2, NIPPON NC-7 OR EQUIVALENT, COMPLETE WITH ALL ACCESSORIES AND INITIAL CHARGE IN FOLLOWING CAPACITIES:
| 5 Kg. | 5 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4.11.3 | SUPPLY & INSTALLATION AND PLACEMENT OF TROLLEY MOUNTED FIRE EXTINGUISHERS, DRY CHEMICAL POWDER TYPE COMPLETE WITH ALL ACCESSORIES & INITIAL CHARGE IN FOLLOWING CAPACITIES:
| 50 Kg. | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5 | SUPPLY & INSTALLATION AND PLACEMENT OF FIRE BLANKETS | 10 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
6 | SUPPLY & INSTALLATION AND PLACEMENT OF SAND BUCKETS (SAND FILLED) WITH STANDS AND SHOVELS. | 8 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7 | AFFF FOAM CONCENTRATE 200 LITRE DRUM FOR WATER/FOAM MONITORS. | 4 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8 | SUPPLY AND INSTALLATION OF SPRINKLERS FOR 8 X EXISTING CONDENSATE STORAGE TANKS AS PER DATASHEETS 165-2-DSM-117 (SPRINKLER DATASHEET). | 1 | LS |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
9 | PUMPS
9.1 | DIESEL ENGINE DRIVEN FW PUMP (P-3501 A/B & 3502)
INSTALLATION, ERECTION, TESTING & COMMISSIONING OF FIRE WATER PUMP, DIESEL ENGINE DRIVEN, MOUNTED ON A COMMON BASE FRAME COMPLETE WITH COUPLING, CONTROL PANEL AND ACCESSORIES AS PER THE FOLLOWING DOCUMENTS / DRAWINGS ATTACHED: REFERENCE DOCUMENTS: 165-2-PID-109 (SHEET 2 OF 4) SEE VENDOR'S DATA FOR PUMPS IN SUPPLEMENTARY TECHNICAL DOCS OF SECTION-V OF TENDER DOCS.
a) | 1500 GPM | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | 750 GPM | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
9.2 | FIRE JOCKEY PUMP (P-3503 A/B)
| INSTALLATION, ERECTION, TESTING & COMMISSIONING OF CENTRIFUGAL PUMP, ELECTRIC MOTOR DRIVEN, MOUNTED ON A COMMON BASE FRAME COMPLETE WITH COUPLING AND ACCESSORIES AS PER THE FOLLOWING DOCUMENTS / DRAWINGS ATTACHED: REFERENCE DOCUMENTS: 165-2-PID-109 (SHEET 2 OF 4) SEE VENDOR'S DATA FOR PUMPS IN SUPPLEMENTARY TECHNICAL DOCS OF SECTION-V OF TENDER DOCS. | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
9.3 | ELECTRIC MOTOR DRIVEN FIRE WATER TANK FILLING PUMP (P-3505 A/B)
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF FOLLOWING CENTRIFUGAL PUMPS COMPLETE WITH MOTOR ASSEMBLIES AND CONTROL PANEL (MOUNTED ON COMMON BASE PLATE) ON RCC FOUNDATIONS. JOB INCLUDES SHIFTING, PLACING IN POSITION, LEVELING, GROUTING, ALIGNMENT, TESTING AND COMMISSIONING OF THE PUMP FOR TROUBLE FREE WORKING INCLUDING COLD & HOT ALIGNMENT CHECKS & WITH FOLLOWING SPECIFICATION | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
FLOWRATE : 425 GPM DIFFERENTIAL HEAD : 35 PSIG REFERENCE DOCUMENT : 165-2-DSM-116 165-2-PID-109 (SHEET 1 OF 4)
10 | RADIOGRAPHIC INSPECTION OF WELDS:
a) | 15 INCH. FILM | - | NOS. | [11 empty] | ONLY FOR RATES
b) | 10 INCH. FILM | - | NOS. | [11 empty] | ONLY FOR RATES
10.1 | ELECTRIC MOTOR DRIVEN DIESEL TRANSFER PUMPS (P-4001 A/B)
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF FOLLOWING CENTRIFUGAL PUMPS COMPLETE WITH MOTOR ASSEMBLIES AND CONTROL PANEL (MOUNTED ON COMMON BASE PLATE) ON RCC FOUNDATIONS. JOB INCLUDES SHIFTING, PLACING IN POSITION, LEVELING, GROUTING, ALIGNMENT, TESTING AND COMMISSIONING OF THE PUMP FOR TROUBLE FREE WORKING INCLUDING COLD & HOT ALIGNMENT CHECKS & WITH FOLLOWING SPECIFICATION | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
FLOWRATE : 10 GPM DIFFERENTIAL HEAD : 40 PSIG REFERENCE DOCUMENT : 165-2-DSM-108 165-2-PID-108
11 | FIXED SKID MOUNTED SCRAPER LAUNCHER
| materials, manufacture, fabrication, assembly, inspection, non-destructive examination, testing and painting.SUPPLY, MANUFACTURE / FABRICATION, INSTALLATION, ASSEMBLY, INSPECTION, TESTING, PAINTING & COMMISSIONING OF SKID MOUNTED 8" x 10" FIXED SCRAPER LAUNCHER SKID ALONGWITH ITS COMPLETE PIPING AND INSTRUMENTATION. REFERENCE DOCUMENT: 165-2-SPM-042 165-2-MPV-001 | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
12 | MISCELLANEOUS
FOLLOWING ITEMS ARE REQUIRED WITH THE ABOVE ITEMS:
a) | START-UP AND COMMISSIONING SPARES (UNIT/SYSTEM WISE LIST WITH ITEM-WISE PRICES TO BE ATTACHED) | 1 | L.S |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
b) | SUPPLY OIF TWO (02) YEARS RECOMMENDED SPARE PARTS. | 1 | L.S |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | OPTIONAL
c) | SUPPLY OF OPERATIONAL CONSUMABLE (DETAILS WITH ITEM-WISE PRICES TO BE ATTACHED) | 1 | L.S |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
TOTAL (Rs.) | [8 empty] | 0 |  |  |  | 0 | 0
Note:
(1) All taxes shall be payable by contractor.
(2) ) The quantities mentioned in the BOQs are indicative and may change as detail design progresses. The bid evaluation will be carried out considering the quantities given in BOQs and unit rates quoted by the Bidders.
(3) Copy of the SRO 678 (1)/2007 is given in Annexure-XV and CGO List given in Attachment-IV of ITB.
(4) Vendor to fill the price in unprotected cells, unprotection of BOQ by bidder lead to disqualification.
(5) Test certificates and MTC's of all items (where applicable) shall be provided.
(6) The charges shall be supported by verified quotation of Inspection Agency.