## Cover Page
|  | Zishan Engineers (Pvt.) Ltd. An ISO 9001-2015 certified company, 47/F, Block 6, PECHS, Karachi-Pakistan Tel: (92-21) 34393045-48 & 34310151-54 Fax: (92-21) 34533430 & 34310156 E-mail : contact@zishanengineers.com, Web : www.zishanengineers.com |  | Document No. | 165-2-BQE-002
|  |  |  | Revision | 0
|  |  |  | Date | 2018-06-04
|  |  |  | Total Pages (inc front cover) | 6
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR LIGHTING, SOCKET OUTLETS,JBs & LOCAL CONTROL STATIONS
0 | 2018-06-04 | Issued for Tender | MF | NAK | MIAH
Rev. | Date | Description | Prepared By | Checked By | Approved By

## BOQ
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR LIGHTING, SOCKETS, LOCAL CONTROL STATIONS
S NO. | D E S C R I P T I O N | QTY. | UNIT | Supply | [5 empty] | Services |  |  |  | Total Amount (Supply + Services) (Pak. Rs.) | REMARKS / REFERENCE
|  |  |  | Unit Rate (Pak Rs.) | Total Supply (Pak Rs.) | GST on Supply items (Pak. Rs.) | Total Supply inclusive of GST | Third Party Pre Shipment Inspection (Pak. Rs.) | Total Supply inclusive of GST & Pre-Shipment Inspection | Unit Rate (Pak Rs.) | Total Services (Pak Rs.) | GST & Provincial tax on Services (Pak.Rs.) | Total Services inclusive of GST & Provincial Tax on Services (Pak.Rs.)
[5 empty] | A | B | C = A+B | D | E = C+D |  | F | G | H = F+G | I=E+H
1 | FLUORESCENT LAMPS (For Hazardous Area)
1.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF, 2X36W, 230V 50HZ FLUORESCENT LIGHT FIXTURE SUITABLE FOR PROTECTION TYPE EEXD' II-C T4, IP-65, GLASS REINFORCED POLYESTER (GRP) ENCLOSURE PROTECTED WITH HIGH IMPACT ACRYLIC POLYCARBONATE DIFFUSER COMPLETE WITH ELECTRONIC BALLAST CONTROL GEAR, 2X36W BI-PIN FLUORESCENT LAMPS, LAMP HOLDERS ETC, INCLUDING PROVISION OF 2 NOS. CABLE ENTRIES OF M20 (FOR FIXTURE TO FIXTURE CABLING). COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | [13 empty] | 165-2-ELT-005
1.1.1 | POLE/STANCHION MOUNTED | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
POLE/STANCHION MOUNTED FIXTURES SHALL BE SUPPLIED WITH INTEGRAL POLE MOUNTING SLEEVE AND ALL MOUNTING AND INSTALLATION ACCESSORIES INCLUDING BRACKETS/CLAMPS COMPLETE IN ALL RESPECTS AND AS PER REFFERED INSTALLTION DETAILS.
1.1.2 | CEILING / SURFACE MOUNTED | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
CEILING/BEAM MOUNTED FIXTURES SHALL BE SUPPLIED WITH MOUNTING ACCESSORIES SUCH AS CLAMPS, BRACKETS, ETC. COMPLETE IN ALL RESPECTS AND AS PER REFFERED INSTALLATION DETAILS.
1.2 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX PROOF, 1X36W, 230V 50HZ FLUORESCENT EMERGENCY LIGHT FIXTURE , NON-MAINTAINED (WITH SELF-TEST FEATURE), NIMH BATTERY BACKUP FOR 1 HOUR, PROTECTION TYPE EEX'D' II-C T4, IP-65, GLASS REINFORCED POLYESTER (GRP) ENCLOSURE PROTECTED WITH HIGH IMPACT ACRYLIC POLYCARBONATE DIFFUSER COMPLETE WITH ELECTRONIC BALLAST, CONTROL GEAR, 1X36W BI-PIN FLUORESCENT LAMPS, LAMP HOLDERS ETC, INCLUDING PROVISION OF 2 NOS. CABLE ENTRIES OF M20 (FOR FIXTURE TO FIXTURE CABLING). COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | [13 empty] | 165-2-ELT-005
1.2.1 | POLE/STANCHION MOUNTED | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
POLE/STANCHION MOUNTED FIXTURES SHALL BE SUPPLIED WITH INTEGRAL POLE MOUNTING SLEEVE AND ALL MOUNTING AND INSTALLATION ACCESSORIES INCLUDING BRACKETS/CLAMPS COMPLETE IN ALL RESPECTS.
1.2.2 | CEILING / SURFACE MOUNTED | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
CEILING/BEAM MOUNTED FIXTURES SHALL BE SUPPLIED WITH MOUNTING ACCESSORIES SUCH AS CLAMPS, BRACKETS, ETC. COMPLETE IN ALL RESPECTS.
2 | FLUORESCENT LIGHTS (FOR NON-HAZARDOUS AREA)
2.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF, 2X36W, 230V, 50HZ, FLUORESCENT LIGHT FIXTURE, GLASS REINFORCED POLYESTER (GRP) ENCLOSURE, IP 65, WITH POLYCARBONATE / ACRYLIC DIFFUSER, COMPLETE WITH ELECTRONIC BALLAST, CONTROL GEAR, 2X36W BI-PIN FLUORESCENT LAMPS, LAMP HOLDERS ETC, INCLUDING PROVISION OF 2 NOS. CABLE ENTRIES M20 (FOR FIXTURE TO FIXTURE CABLING).COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | [13 empty] | 165-2-ELT-005
2.1.1 | POLE/STANCHION MOUNTED | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
POLE/STANCHION MOUNTED FIXTURES SHALL BE SUPPLIED WITH INTEGRAL POLE MOUNTING SLEEVE AND ALL MOUNTING AND INSTALLATION ACCESSORIES INCLUDING BRACKETS/CLAMPS COMPLETE IN ALL RESPECTS.
2.1.2 | CEILING / SURFACE MOUNTED | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
CEILING/BEAM MOUNTED FIXTURES SHALL BE SUPPLIED WITH MOUNTING ACCESSORIES SUCH AS CLAMPS, BRACKETS, ETC. COMPLETE IN ALL RESPECTS.
2.2 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF, 1X36W, 230V, 50HZ, FLUORESCENT EMERGENCY LIGHT FIXTURE , NON-MAINTAINED (WITH SELF-TEST FEATURE), NIMH BATTERY BACKUP FOR 1 HOUR, GLASS REINFORCED POLYESTER (GRP) ENCLOSURE, IP 65, WITH POLYCARBONATE / ACRYLIC DIFFUSER, COMPLETE WITH ELECTRONIC BALLAST, CONTROL GEAR, 1X36W BI-PIN FLUORESCENT LAMPS, LAMP HOLDERS ETC, INCLUDING PROVISION OF 2 NOS. CABLE ENTRIES M20 (FOR FIXTURE TO FIXTURE CABLING). COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | [13 empty] | 165-2-ELT-005
2.2.1 | POLE/STANCHION MOUNTED | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
POLE/STANCHION MOUNTED FIXTURES SHALL BE SUPPLIED WITH INTEGRAL POLE MOUNTING SLEEVE AND ALL MOUNTING AND INSTALLATION ACCESSORIES INCLUDING BRACKETS/CLAMPS COMPLETE IN ALL RESPECTS.
2.2.2 | CEILING / SURFACE MOUNTED | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
CEILING/BEAM MOUNTED FIXTURES SHALL BE SUPPLIED WITH MOUNTING ACCESSORIES SUCH AS CLAMPS, BRACKETS, ETC. COMPLETE IN ALL RESPECTS.
3 | FLOOD LIGHTS (FOR HAZARDOUS AREA)
3.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF 400W- 230V AC-50HZ FLOOD LIGHT FIXTURE SUITABLE FOR PROTECTION TYPE EEX "n"' II-C T4 ,IP-65, POLE TOP MOUNTED, WITH INTEGRAL CONTROL GEAR, GLASS REINFORCED POLYESTER (GRP) OR DIE-CAST ALUMINIUM ENCLOSURE COMPLETE WITH BALLAST/ STARTERS/ CAPACITORS, 400W SON T(BS 4533) LAMP, ASYMMETRICAL REFLECTOR. CABLE ENTRIES OF M20 SHALL BE PROVIDED FOR FIXTURE TO FIXTURE WIRING (LOOP/THROUGH WIRING). ALL MOUNTING ACCESSORIES SHALL BE SUPPLIED WITH FIXTURE. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 33 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-005
4 | FLOOD LIGHTS (FOR NON-HAZARDOUS AREA)
4.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF 400W- 230V AC-50HZ FLOOD LIGHT FIXTURE, IP-65, POLE TOP MOUNTED, WITH INTEGRAL CONTROL GEAR, GLASS REINFORCED POLYESTER (GRP) OR DIE-CAST ALUMINIUM ENCLOSURE COMPLETE WITH BALLAST/ STARTERS/ CAPACITORS, 400W SON T(BS 4533) LAMP, ANODIZED ALUMINIUM REFLECTOR (ASYMMETRICAL). CABLE ENTRIES OF M20 SHALL BE PROVIDED FOR FIXTURE TO FIXTURE WIRING (LOOP/THROUGH WIRING).ALL MOUNTING ACCESSORIES SHALL BE SUPPLIED WITH FIXTURE. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 33 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-005
5.0 | LIGHTING POLES
| SUPPLY, INSTALLATION, TESTING, ERECTION AND COMMISSIONING OF LIGHTING POLE FOR FLOODLIGHTING, MADE OF GALVANIZED STEEL PIPE, 10 METER HIGH WITH ARMS FOR MULTIPLE 400 WATT FLOODLIGHTS WELD ON THE TOP OF THE POLE AS SHOWN ON TYPICAL DETAIL DRAWING, COMPLETE WITH BASE PLATE, EARTHING BOSS ETC. AND OTHER ACCESSORIES. THE JOB ALSO INCLUDES CONSTRUCTION OF FOUNDATIONS AND ALL OTHER RELATED CIVIL WORKS COMPLETE IN ALL RESPECTS | [13 empty] | 165-2-ELT-005
5.1 | TYPE-A (2 FLOOD LIGHTS PER POLE) | 1 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5.2 | TYPE-B (3 FLOOD LIGHTS PER POLE) | 22 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5.3 | TYPE-C (4 FLOOD LIGHTS PER POLE) | 1 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
6 | JUNCTION BOX (FOR HAZARDOUS AREA)
6.1 | JUNCTION BOX FOR LIGHTING
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF JUNCTION BOX FOR LIGHTING SUITABLE FOR HAZARDOUS AREA, EEX'E' II-C T4, IP65, IMPACT RESISTANT POLYESTER ENCLOSURE, WITH TERMINALS SUITABLE FOR 2.5MM2 TO 25MM2 STRANDED CONDUCTORS AS SHOWN IN THE REFERRED JB SCHEDULE, EARTHING TERMINAL RAIL, WITH SUITABLE CABLE ENTRIES AND INSTALLATION ACCESSORIES COMPLETE IN ALL RESPECT ALONG WITH INTERNAL WIRING AND TERMINATIONS. THE JB SHALL HAVE METALLIC GLAND PLATES, LOCKNUTS & WASHERS AND ALL OTHER ACCESSORIES REQUIRED FOR INSTALLATION AND AS PER REFFERED INSTALLATION DETAILS AND ACCEPTED INDUSTRY PRACTICES. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 12 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-002
6.2 | JUNCTION BOX FOR UTILITY SOCKET OUTLET
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF JUNCTION BOX FOR UTILITY OUTLETS SUITABLE FOR HAZARDOUS AREA, EEX'E' II-C T4, IP65, IMPACT RESISTANT POLYESTER ENCLOSURE, WITH TERMINALS SUITABLE FOR 2.5MM2 TO 25MM2 STRANDED CONDUCTORS AS SHOWN IN THE REFERRED JB SCHEDULE, EARTHING TERMINAL RAIL, WITH SUITABLE CABLE ENTRIES AND INSTALLATION ACCESSORIES COMPLETE IN ALL RESPECT ALONG WITH INTERNAL WIRING AND TERMINATIONS. THE JB SHALL HAVE METALLIC GLAND PLATES, LOCKNUTS & WASHERS AND ALL OTHER ACCESSORIES REQUIRED FOR INSTALLATION AS PER REFERRED ANNEXURES AND ACCEPTED INDUSTRY PRACTICES. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-002
7 | JUNCTION BOX (FOR NON-HAZARDOUS AREA)
7.1 | JUNCTION BOX FOR LIGHTING
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF JUNCTION BOX FOR LIGHTING, IP55 (MIN), UV STABILIZED POLYCARBONATE OR SHEET METAL ENCLOSURE, WITH TERMINALS SUITABLE FOR 2.5MM2 TO 25MM2 STRANDED CONDUCTORS AS SHOWN IN THE REFERRED JB SCHEDULE, EARTHING TERMINAL RAIL, WITH SUITABLE CABLE ENTRIES AND INSTALLATION ACCESSORIES COMPLETE IN ALL RESPECT ALONG WITH INTERNAL WIRING AND TERMINATIONS. THE JB SHALL HAVE METALLIC GLAND PLATES, LOCKNUTS & WASHERS AND ALL OTHER ACCESSORIES REQUIRED FOR INSTALLATION AS PER REFERRED ANNEXURES AND ACCEPTED INDUSTRY PRACTICES. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 12 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-002
7.2 | JUNCTION BOX FOR UTILITY SOCKET OUTLET
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF JUNCTION BOX FOR UTILITY OUTLETS, IP55 (MIN), UV STABILIZED POLYCARBONATE OR SHEET METAL ENCLOSURE, WITH TERMINALS SUITABLE FOR 2.5MM2 TO 16MM2 STRANDED CONDUCTORS AS SHOWN IN THE REFERRED JB SCHEDULE, EARTHING TERMINAL RAIL, WITH SUITABLE CABLE ENTRIES AND INSTALLATION ACCESSORIES COMPLETE IN ALL RESPECT ALONG WITH INTERNAL WIRING AND TERMINATIONS. THE JB SHALL HAVE METALLIC GLAND PLATES, LOCKNUTS & WASHERS AND ALL OTHER ACCESSORIES REQUIRED FOR INSTALLATION AS PER REFERRED ANNEXURES AND ACCEPTED INDUSTRY PRACTICES. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-002
8 | UTILITY SOCKET OUTLETS (FOR HAZARDOUS AREA)
8.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF SWITCHED UTILITY OUTLETS 16A, SINGLE PHASE 3-PIN 230V, PROTECTION TYPE EEX'D' II-C T4, IP-65 GRP POLYAMIDE ENCLOSURE, COMPLETE WITH 2 NOS. CABLE ENTRIES OF M25 (WITH STOPPING PLUGS), MATCHING PLUGS AND INTERNAL TERMINAL BLOCK. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 5 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-003
8.2 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF SWITCHED UTILITY OUTLETS 16A, SINGLE PHASE 3-PIN 230V, PROTECTION TYPE EEX'n' II-C T4, IP-65 GRP POLYAMIDE ENCLOSURE, COMPLETE WITH 2 NOS. CABLE ENTRIES OF M25 (WITH STOPPING PLUGS), MATCHING PLUGS AND INTERNAL TERMINAL BLOCK. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-003
9 | UTILITY SOCKET OUTLETS (FOR NON-HAZARDOUS AREA)
9.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF SWITCHED UTILITY OUTLETS 16A, SINGLE PHASE 3-PIN 230V, IP-65 UV STABILIZED POLYCARBONATE ENCLOSURE, COMPLETE WITH 2 NOS. CABLE ENTRIES OF M25 (WITH STOPPING PLUGS), MATCHING PLUGS AND INTERNAL TERMINAL BLOCK. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-003
10 | WELDING SOCKET OUTLETS (FOR HAZARDOUS AREA)
10.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF SWITCHED WELDING SOCKET OUTLET 63A, THREE PHASE 5-PIN 400V, PROTECTION TYPE EEX'D' II-C T4, IP-65 GRP POLYAMIDE ENCLOSURE, COMPLETE WITH 1 NO CABLE ENTRY OF M32 (WITH STOPPING PLUG), MATCHING PLUGS AND INTERNAL TERMINAL BLOCK. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-003
10.2 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF EX-PROOF SWITCHED WELDING SOCKET OUTLET 63A, THREE PHASE 5-PIN 400V, PROTECTION TYPE EEX'n' II-C T4, IP-65 GRP POLYAMIDE ENCLOSURE, COMPLETE WITH 1 NO CABLE ENTRY OF M32 (WITH STOPPING PLUG), MATCHING PLUGS AND INTERNAL TERMINAL BLOCK. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-003
11 | WELDING SOCKET OUTLETS (FOR NON-HAZARDOUS AREA)
11.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF WEATHER PROOF SWITCHED WELDING SOCKET OUTLET 63A, THREE PHASE 5-PIN 400V, IP-65 UV STABILIZED POLYCARBONATE ENCLOSURE, COMPLETE WITH 1 NO CABLE ENTRY OF M32 (WITH STOPPING PLUG), MATCHING PLUGS AND INTERNAL TERMINAL BLOCK. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-003
12 | LOCAL CONTROL STATIONS (FOR HAZARDOUS AREA).
12.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF LOCAL CONTROL STATION (OF FOLLOWING TYPE) FOR LV MOTORS, EEX'N' IIC T4, IP-65. GRP POLYCARBONATE ENCLOSURE, COMPLETE WITH CABLE ENTRY OF M25 (WITH STOPPING PLUG) FOR 12C-2.5MM2 ARMOURED CABLE. LOCAL CONTROL STATION SHALL BE SUPPLIED COMPLETE WITH ALL REQUIRED INTERNAL TERMINALS, EARTHING TERMINALS, GLAND PLATE, NUTS, BOLTS, WASHERS, ETC COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | [13 empty] | 165-2-ELT-004
| THREE POSITION (I-O-II) ROTARY SELECTOR SWITCH FOR MANUAL-OFF-AUTO (MOA) SELECTION AND COMPRISING OF 1 NO. ON PUSH BUTTON (MOMENTARY CONTACT), 1 NO. MUSHROOM STAYPUT (LATCHED CONTACT) TYPE OFF PUSH BUTTON AND 2 NO. GREEN AND RED INDICATION LAMP. | 2 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
13 | LOCAL CONTROL STATIONS (FOR NON- HAZARDOUS AREA).
13.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF LOCAL CONTROL STATION (OF FOLLOWING TYPE) FOR LV MOTORS, IP-55. UV STABILIZED POLYCARBONATE ENCLOSURE, COMPLETE WITH CABLE ENTRY OF M25 (WITH STOPPING PLUG) FOR 12C-2.5MM2 ARMOURED CABLE. LOCAL CONTROL STATION SHALL BE SUPPLIED COMPLETE WITH ALL REQUIRED INTERNAL TERMINALS, EARTHING TERMINALS, GLAND PLATE, NUTS, BOLTS, WASHERS, ETC. COMPLETE IN ALL RESPECT AND AS PER REFFERED TYPICAL INSTALLATION DRAWING. | [13 empty] | 165-2-ELT-004
| THREE POSITION (I-O-II) ROTARY SELECTOR SWITCH FOR MANUAL-OFF-AUTO (MOA) SELECTION AND COMPRISING OF 1 NO. ON PUSH BUTTON (MOMENTARY CONTACT), 1 NO. MUSHROOM STAYPUT (LATCHED CONTACT) TYPE OFF PUSH BUTTON AND 1 NO. GREEN INDICATION LAMP. | 2 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
14 | MULTIPLE SOCKET ASSEMBLIES (FOR HAZARDOUS AREA).
14.1 | SUPPLY OF EX-PROOF MULTIPLE SOCKET ASSEMBLIES, SUITABLE FOR USE AS A PORTABLE SUPPLY POINT IN CLASS I, DIV 1 CLASSIFIED HAZARDOUS AREA. THIS INCLUDES A COMMON ENCLOSURE RATED EEX de IIC T4, IP65 MADE OF GRP OR METAL COMPLETE WITH FOLLOWING COMPONENTS. - 63A, 5 PIN SOCKET INLET FOR RECEIVING POWER CONNECTION. - 63 A 3P MCB AS INCOMING PROTECTION. - 2 NOS 16A 3 PIN SWITCHED SOCKET OUTLET COMPLETE WITH 1P MCB. -1 NOS 32A 5 PIN SWITCHED SOCKET OUTLET. COMPLETE WITH 3P MCB. | 1 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-004
| Total Price (1 to 14) | [7 empty] | 0 |  |  |  | 0 | 0
NOTES:
1 | All taxes shall be payable by contractor.
2 | The quantities mentioned in the BOQs are indicative and may change as detail design progresses. The bid evaluation will be carried out considering the quantities given in BOQs and unit rates quoted by the Bidders.
3 | Test certificates and MTC's of all items (where applicable) shall be provided.
4 | The charges shall be supported by verified quotation of Inspection Agency.
5 | Copy of the SRO 678 (1)/2007 is given in Annexure-XVIII