## Cover Page
|  | Zishan Engineers (Pvt.) Ltd. An ISO 9001-2015 certified company, 47/F, Block 6, PECHS, Karachi-Pakistan Tel: (92-21) 34393045-48 & 34310151-54 Fax: (92-21) 34533430 & 34310156 E-mail : contact@zishanengineers.com, Web : www.zishanengineers.com |  | Document No. | 165-2-BQE-001
|  |  |  | Revision | 0
|  |  |  | Date | 2018-06-04
|  |  |  | Total Pages (inc front cover) | 4
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR ELECTRICAL CABLES
0 | 2018-06-04 | Issued for Tender | MF | NAK | MIAH
Rev. | Date | Description | Prepared By | Checked By | Approved By

## BOQ
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR ELECTRICAL CABLES OF GAS PROCESSING PLANT
S.NO. | D E S C R I P T I O N | QTY. | UNIT | Supply | [5 empty] | Services |  |  |  | Total Amount (Supply + Services) (Pak. Rs.) | REMARKS / REFERENCE
|  |  |  | Unit Rate (Pak Rs.) | Total Supply (Pak Rs.) | GST on Supply items (Pak. Rs.) | Total Supply inclusive of GST | Third Party Pre Shipment Inspection (Pak. Rs.) | Total Supply inclusive of GST & Pre-Shipment Inspection | Unit Rate (Pak Rs.) | Total Services (Pak Rs.) | GST & Provincial tax on Services (Pak.Rs.) | Total Services inclusive of GST & Provincial Tax on Services (Pak.Rs.)
[5 empty] | A | B | C = A+B | D | E = C+D |  | F | G | H = F+G | I=E+H
1.0 | SUPPLY & INSTALLATION OF ELECTRICAL CABLE
| SUPPLY, LAYING, DRESSING, TAGGING, TERMINATION, TESTING AND COMMISSIONING OF FOLLOWING ELECTRICAL POWER, CONTROL AND LIGHTING CABLE (AS PER REFERRED CABLE SCHEDULES, SPECIFICATIONS AND TYPICAL INSTALLATION DRAWINGS) ON CABLE LADDER / RACKS/ M.S CHANNEL, CONDUITS, TRENCHES COMPLETE IN ALL RESPECTS INCLUDING INSTALLATION OF CABLE LUGS, TERMINATION OF ARMOUR (IF AVAILABLE) THROUGH GLAND / PLATE UPTO THE EARTH TERMINAL OF EQUIPMENT, TAGGING WITH ALPHA NUMERIC PLASTIC FERRULES, ETC. COMPLETE IN ALL RESPECT | [13 empty] | 165-2-SPE-021 165-2-SPE-023 165-2-SPE-025 & All Typical Installation drawings
1.1 | SINGLE CORE ARMOURED LOW VOLTAGE CABLES (FOR POWER APPLICATIONS).
SINGLE CORE LOW VOLTAGE POWER CABLES, STRANDED COPPER CONDUCTOR AS PER IEC-60502, CROSS LINKED POLY ETHYLENE INSULATED 600/1000 VOLT GRADE, NON-HYGROSCOPIC FILLERS, EXTRUDED POLYVINYL CHLORIDE BEDDED AND SINGLE ALUMINIUM WIRE ARMOURED POLYVINYL CHLORIDE SHEATHED OVERALL.
1.1.1 | 1C - 240 SQMM (CU/XLPE/PVC/AWA/PVC) | 3300 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.1.2 | 1C - 300 SQMM (CU/XLPE/PVC/AWA/PVC) | 1260 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2 | MULTI CORE ARMOURED LOW VOLTAGE CABLES (FOR POWER APPLICATIONS).
MULTI CORE LOW VOLTAGE POWER CABLES, STRANDED COPPER CONDUCTOR AS PER IEC-60502, CROSS LINKED POLY ETHYLENE INSULATED 600/1000 VOLT GRADE, NON-HYGROSCOPIC FILLERS, EXTRUDED POLYVINYL CHLORIDE BEDDED, SINGLE STEEL WIRE ARMOURED AND POLYVINYL CHLORIDE SHEATHED OVERALL.
1.2.1 | 2C - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 2170 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.2 | 2C - 4 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.3 | 2C - 6 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.4 | 2C - 10 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.5 | 2C+PE - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 3570 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.6 | 2C+PE - 4 SQMM (CU/XLPE/PVC/SWA/PVC) | 860 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.7 | 2C+PE - 10 SQMM (CU/XLPE/PVC/SWA/PVC) | 1032 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.8 | 2C+PE - 25 SQMM (CU/XLPE/PVC/SWA/PVC) | 195 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.9 | 2C+PE - 35 SQMM (CU/XLPE/PVC/SWA/PVC) | 165 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.10 | 3C - 4.0 SQMM (CU/XLPE/PVC/SWA/PVC) | 1166 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.11 | 3C - 6.0 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.12 | 3C - 10 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.13 | 3C - 16 SQMM (CU/XLPE/PVC/SWA/PVC) | 180 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.14 | 3C - 25 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.15 | 3C - 35 SQMM (CU/XLPE/PVC/SWA/PVC) | 940 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.16 | 3C - 50 SQMM (CU/XLPE/PVC/SWA/PVC) | 988 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.17 | 3C - 70 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.18 | 4C - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.19 | 4C - 4 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.20 | 4C - 6 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.21 | 4C - 10 SQMM (CU/XLPE/PVC/SWA/PVC) | 1747 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.22 | 4C - 16 SQMM (CUXLPE//PVC/SWA/PVC) | 190 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.23 | 4C - 25 SQMM (CU/XLPE/PVC/SWA/PVC) | 35 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.24 | 4C - 35 SQMM (CU/XLPE/PVC/SWA/PVC) | 1030 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.25 | 4C - 50 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.26 | 4C - 70 SQMM (CU/XLPE/PVC/SWA/PVC) | 30 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.27 | 4C - 95 SQMM (CU/XLPE/PVC/SWA/PVC) | 495 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.28 | 4C - 120 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.29 | 4C - 240 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.30 | 4C - 300 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
NOTE: THE COLOR CODING FOR THE ABOVE MULTI CORE CABLES SHALL BE AS FOLLOWS:
FOR 1C CABLES - RED OR YELLOW OR BLUE OR BLACK AS PER CABLE SCHEDULE
FOR 2C CABLES - RED AND BLACK
FOR 3C CABLES - RED , YELLOW & BLUE
FOR 4C CABLES - RED , YELLOW, BLUE & BLACK
FOR 2C+PE CABLES - IT SHOULD BE 3C CABLE WITH OVERALL ARMORING AND SHEAT, RED FOR PHASE, BLACK FOR NEUTRAL & GREEN FOR EARTH
1.3 | ARMOURED LOW VOLTAGE CABLES (FOR CONTROL APPLICATIONS).
LOW VOLTAGE CONTROL CABLES, STRANDED COPPER CONDUCTOR, CROSS LINKED POLY ETHYLENE INSULATED, 600/1000 VOLT GRADE, POLYVINYL CHLORIDE BEDDED, SINGLE STEEL WIRE ARMOURED AND POLYVINYL CHLORIDE SHEATHED OVERALL. (TO BS 6346 / IEC60502)
1.3.1 | 7C - 1.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 840 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.2 | 10C - 1.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 840 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.3 | 12C - 1.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.4 | 14C - 1.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.5 | 7C - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.6 | 10C - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 50 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.7 | 12C - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 900 | RMTRS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.3.8 | 14C - 2.5 SQMM (CU/XLPE/PVC/SWA/PVC) | 1270 | RMTRS.
1.4 | CABLE GLANDS (FOR HAZARDOUS AREA)
SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF BRASS CABLE GLANDS OF FOLLOWING SIZES CONFORMING TO BS 6121 AND SUITABLE FOR CU/XLPE/PVC/SWA/PVC LOW VOLTAGE CABLES. GLANDS TO BE SUPPLIED COMPLETE WITH PCP SHROUD AND SHALL BE, E1FW, DUAL CERTIFIED (EX'E' / EX'D') SUITABLE FOR CLASS I, ZONE 1 & 2, IP 66 APPLICATIONS. COMPLETE IN ALL RESPECT AND AS PER REFFERED CABLE SCHEDULE
1.4.1 | E1FW 20 | 52 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.4.2 | E1FW 25 | 45 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.4.3 | E1FW 32 | 6 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.4.4 | E1FW 40 | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.4.5 | E1FW 50 | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.4.6 | E1FW 50S | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.4.7 | E1FW 63 | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5 | CABLE GLANDS (FOR NON HAZARDOUS AREA)
SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF BRASS CABLE GLANDS OF FOLLOWING SIZES CONFORMING TO BS 6121 AND SUITABLE FOR LOW VOLTAGE CABLES. GLANDS TO BE SUPPLIED COMPLETE WITH PCP SHROUD AND SHALL BE E1W, WEATHERPROOF, SUITABLE FOR IP 66 APPLICATIONS. . COMPLETE IN ALL RESPECT AND AS PER REFFERED CABLE SCHEDULE
1.5.1 | E1W 20 | 99 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.2 | E1W 20S | 10 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.3 | E1W 25 | 21 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.4 | E1W 32 | 34 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.5 | E1W 50 | 114 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.6 | E1W 50S | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.7 | E1W 63 | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.5.8 | E1W 63S | 3 | NOS. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
TOTAL PRICE (1.1 - 1.5) |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 0
NOTES:
1 | ALL TAXES SHALL BE PAYABLE BY CONTRACTOR.
2 | THE QUANTITIES MENTIONED IN THE BOQS ARE INDICATIVE AND MAY CHANGE AS DETAIL DESIGN PROGRESSES. THE BID EVALUATION WILL BE CARRIED OUT CONSIDERING THE QUANTITIES GIVEN IN BOQS AND UNIT RATES QUOTED BY THE BIDDERS.
3 | TEST CERTIFICATES AND MTC'S OF ALL ITEMS (WHERE APPLICABLE) SHALL BE PROVIDED.
4 | THE CHARGES SHALL BE SUPPORTED BY VERIFIED QUOTATION OF INSPECTION AGENCY.
5 | COPY OF THE SRO 678 (1)/2007 IS GIVEN IN ANNEXURE-XVIII
6 | THE BRASS REDUCERS AND ADOPTERS HAZARDOUS AND NON HAZARDOUS TYPE SHALL BE CONSIDERD BUILT IN FOR SECTION 1.4 AND 1.5 AS PER SITE REQUIRMENT AND ARE INCLUDED IN THE SCOPE OF CONTRACTOR