## Cover Page
|  | Zishan Engineers (Pvt.) Ltd. An ISO 9001-2015 certified company, 47/F, Block 6, PECHS, Karachi-Pakistan Tel: (92-21) 34393045-48 & 34310151-54 Fax: (92-21) 34533430 & 34310156 E-mail : contact@zishanengineers.com, Web : www.zishanengineers.com |  | Document No. | 165-2-BQE-005
|  |  |  | Revision | 0
|  |  |  | Date | 2018-06-04
|  |  |  | Total Pages (inc front cover) | 3
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR EARTHING WORKS
0 | 2018-06-04 | Issued for Tender | MF | NAK | MIAH
Rev. | Date | Description | Prepared By | Checked By | Approved By

## BQE
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR EARTHING WORKS
S. NO. | DESCRIPTION | QTY. | UNIT | Supply | [5 empty] | Services |  |  |  | Total Amount (Supply + Services) (Pak. Rs.) | REMARKS / REFERENCE
|  |  |  | Unit Rate (Pak Rs.) | Total Supply (Pak Rs.) | GST on Supply items (Pak. Rs.) | Total Supply inclusive of GST | Third Party Pre Shipment Inspection (Pak. Rs.) | Total Supply inclusive of GST & Pre-Shipment Inspection | Unit Rate (Pak Rs.) | Total Services (Pak Rs.) | GST & Provincial tax on Services (Pak.Rs.) | Total Services inclusive of GST & Provincial Tax on Services (Pak.Rs.)
[5 empty] | A | B | C = A+B | D | E = C+D |  | F | G | H = F+G | I=E+H
1.0 | SUPPLY, INSTALLATION,TESTING & COMMISIONING OF 4M LONG EARTH ELECTRODE, COPPER CLADDED STEEL, 3/4" DIA ROD, WITH 2 M LONG AND 2" DIA UPVC PIPE, EXTENDIBLE ON BOTH SIDES COMPLETE WITH DRIVING HEAD CAP ON TOP, 2 NOS. CLAMPS FOR 70 SQ.MM BARE CONDUCTOR CONNECTION, STAINLESS STEEL FASTENING ACCESSORIES ETC. COMPLETE IN ALL RESPECT. THE JOB INCLUDES CONSTRUCTION OF CONCRETE EARTH PIT WITH ALL MATERIALS AS SHOWN IN REFER DRAWING COMPLETE IN ALL RESPECT. | 6 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
2.0 | SAME AS ITEM#1, BUT WITHOUT CONSTRUCTION OF EARTHPIT. (RODS TO BE BURIED) | 8 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
3.0 | SUPPLY, INSTALLATION,TESTING & COMMISIONING OF 6M LONG EARTH ELECTRODE, COPPER CLADED, 3/4" DIA ROD, WITH 3 M LONG AND 2' DIA UPVC PIPE, EXTENDIBLE ON BOTH SIDES COMPLETE WITH DRIVING HEAD CAP ON TOP, 2 NOS. CLAMPS FOR 70 SQ.MM BARE CONDUCTOR CONNECTION, STAINLESS STEEL FASTENING ACCESSORIES ETC. COMPLETE IN ALL RESPECT. THE JOB INCLUDES CONSTRUCTION OF CONCRETE EARTH PIT WITH ALL MATERIALS AS SHOWN IN REFER DRAWING COMPLETE IN ALL RESPECT. | 3 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
4.0 | SUPPLY, INSTALLATION,TESTING & COMMISIONING OF EARTH BARS MADE OF HARD DRAWN COPPER (TINNED), SUITABLE FOR MOUNTING ON STEEL STRUCTURE, CONSISTING OF 10 NOS. EQUALLY SPACED M8 HOLES. EACH PLATE SHALL ALSO HAVE 2 NOS. M10 HOLES FOR MOUNTING. EACH PLATE SHALL BE SUPPLIED WITH 2 NOS. GALVANIZED MILD STEEL TUBE SPACERS, AND M10, ELECTROZINC PLATED NUTS, BOLTS AND STAR WASHERS, COMPLETE IN ALL RESPECTS. | 12 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
5.0 | SUPPLY, INSTALLATION,TESTING & COMMISIONING OF PVC-INSULATED, GREEN-YELLOW OUTER PVC SHEATHED, CIRCULAR, STRANDED ANNEALED COPPER CONDUCTOR CABLES, CONFIRMING TO BS-6004, (450 / 750 V) ON CABLE LADDER / RACK OR BURIED COMPLETE IN ALL RESPECTS INCLUDING SUPPLY AND INSTALLATION OF CRIMPED CONNECTORS FOR BRANCHING OF ABOVE GROUND EARTH CABLE, SUPPLY AND INSTALLATION CABLE LUGS AND TERMINATIONS ON EQUIPMENT AND EARTHING PHILOSOPHY DOCUMENTS. | [13 empty] | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
5.1 | 1C-240 | 70 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5.2 | 1C-70 | 180 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5.3 | 1C-35 | 120 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5.4 | 1C-16 | 40 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5.5 | 1C-6 | 240 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
6.0 | SUPPLY AND INSTALLATION OF CAD WELD CONNECTIONS ON BURIED CABLE OF FOLLOWING SIZES | [13 empty] | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
6.1 | 1C-70 | 6 | Nos |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
6.2 | 1C-35 | 12 | Nos |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
6.3 | 1C-16 | 10 | Nos |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.0 | SUPPLY, INSTALLATION, LAYING, TERMINATION, TESTING AND COMMISSIONING OF FOLLOWING SIZES BARE COPPER CONDUCTORS (TO IEC 60228) COMPLETE IN ALL RESPECTS. CONDUCTOR TO BE LAID ON LEAN CONCRETED SURFACE. THIS ALSO INCLUDES CABLE TERMINATION / CLAMPING ON ABOVE EARTH RODS, INSTALLATION OF STUB-UP PIPES FOR BRINGING THE CABLE ABOVE SURFACE AND TERMINATION ON STEEL STRUCTURE OR EARTH PLATES ETC. AS SPECIFIED ON EARTHING SCHEMATICS. | [13 empty] | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
7.1 | 1C-70 | 50 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.2 | 1C-35 | 60 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.3 | 1C-10 | 80 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.4 | 1C-6 | 100 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8 | SUPPLY, INSTALLATION,TESTING & COMMISIONING OF C-TYPE, COPPER COMPRESSION TAPS / CONNECTOR FOR CRIMPED CONNECTIONS OF EARTH CABLE BRANCHES FROM MAIN CABLE. CONNECTORS SHALL BE SUITABLE FOR FOLLOWING CABLE SIZES. | [13 empty] | 165-2-ELT-001 165-2-SPE-023 165-2-SPE-021
8.1 | MAIN 70 SQMM; BRANCH 70 SQMM | 2 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8.2 | MAIN 70 SQMM; BRANCH 35 SQMM | 11 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8.3 | MAIN 70 SQMM; BRANCH 16 SQMM | 3 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8.4 | MAIN 35 SQMM; BRANCH 35 SQMM | 2 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8.5 | MAIN 35 SQMM; BRANCH 16 SQMM | 8 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8.6 | MAIN 16 SQMM; BRANCH 16 SQMM | 2 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
9.0 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF ANNEALED COPPER STRIP 20 mm x 3 mmT IN HORIZONAL MESH FORMAT ON TOP OF DIFFERENT BUILDINGS INCLUDING CONNECTION OF THE NETWORK WITH STEEL BARS OF ROOF RCC STRUCTURE COMPLETE IN ALL RESPECTS INCLUDING ALL INSTALLATION ACCESSORIES SUCH AS CLAMPS, NUTS, BOLTS ETC. THE JOB INCLUDES SECURELY CONNECTING ALL MUTUALLY CROSSING STRIPS AT INTERSECTION POINTS AS PER REFFERED INSTALLATION DETAILS. | 30 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELT-008 165-2-SPE-023 165-2-SPE-021
10.0 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF ANNEALED COPPER STRIP 20 mm x 3 mmT AS DOWN CONDUCTOR OF LP SYSTEM. THIS INCLUDES CLAMPING ON EXTERNAL WALL AND CONNECTION WITH THE EARTH AND RCC STRUCTURE NETWORK. | 4 | RMtrs. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
11.0 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF LP TEST POINTS. | 3 | Nos. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
12 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF COMPLETE IMPRESSED CURRENT CATHODIC PROTECTION FOR 2 NOS OF TANKS AT MELA FACILITY COMPLETE IN ALL RESPECTS AS DETAILED IN SCOPE OF WORK AND SPECIFICATION FOR CP SYSTEM (165-2-SPE-026). THE JOB INCLUDES BUT NOT LIMITED TO COMPLETE ANODE, RECTIFIER, TRANSFORMER, ALL CABLINGS, TEST POINTS, CONTROL PANEL ETC ETC REQUIRED FOR COMPLETE CATHODIC PROTECTION SYSTEM. | 1 | JOB |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
13 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF COMPLETE SACRIFICIAL ANODE CATHODIC PROTECTION FOR COMPLETE PLANT BURIED PIPINGS AS PER ATTACHED PIPING LAYOUTS AND P&IDs AT MELA FACILITY COMPLETE IN ALL RESPECTS AS DETAILED IN SCOPE OF WORK AND SPECIFICATION FOR CP SYSTEM (165-2-SPE-026). THE JOB INCLUDES BUT NOT LIMITED TO COMPLETE ANODE, ALL CABLINGS, TEST POINTS ETC REQUIRED FOR COMPLETE CATHODIC PROTECTION SYSTEM. | 1 | JOB |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
| Total Price (1 to 13) | [7 empty] | 0 |  |  |  | 0 | 0
NOTES:
1 | All taxes shall be payable by contractor.
2 | The quantities mentioned in the BOQs are indicative and may change as detail design progresses. The bid evaluation will be carried out considering the quantities given in BOQs and unit rates quoted by the Bidders.
3 | Test certificates and MTC's of all items (where applicable) shall be provided.
4 | The charges shall be supported by verified quotation of Inspection Agency.