## Cover Page
|  | Zishan Engineers (Pvt.) Ltd. An ISO 9001-2015 certified company, 47/F, Block 6, PECHS, Karachi-Pakistan Tel: (92-21) 34393045-48 & 34310151-54 Fax: (92-21) 34533430 & 34310156 E-mail : contact@zishanengineers.com, Web : www.zishanengineers.com |  | Document No. | 165-2-BQE-004
|  |  |  | Revision | 0
|  |  |  | Date | 2018-06-04
|  |  |  | Total Pages (inc front cover) | 5
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR BUILDINGS
0 | 2018-06-04 | Issued for Tender | MF | NAK | MIAH
Rev. | Date | Description | Prepared By | Checked By | Approved By

## BOQ-I ELECTRICAL WORKS
OIL & GAS DEVELOPMENT COMPANY LTD.
MELA DEVELOPMENT PROJECT
BILL OF QUANTITIES FOR BUILDINGS
ITEM # | DESCRIPTION | QTY | UNIT | Supply | [5 empty] | Services |  |  |  | Total Amount (Supply + Services) (Pak. Rs.) | REMARKS / REFERENCE
|  |  |  | Unit Rate (Pak Rs.) | Total Supply (Pak Rs.) | GST on Supply items (Pak. Rs.) | Total Supply inclusive of GST | Third Party Pre Shipment Inspection (Pak. Rs.) | Total Supply inclusive of GST & Pre-Shipment Inspection | Unit Rate (Pak Rs.) | Total Services (Pak Rs.) | GST & Provincial tax on Services (Pak.Rs.) | Total Services inclusive of GST & Provincial Tax on Services (Pak.Rs.)
[5 empty] | A | B | C = A+B | D | E = C+D |  | F | G | H = F+G | I=E+H
1 | WIRING / WIRING ACCESSORIES
| PROVIDING, INSTALLATION, TESTING & COMMISSIONING OF FOLLOWING ITEMS INCLUDING ALL MATERIAL, TOOLS, LABOR & ACCESSORIES REQUIRED FOR COMPLETION OF WORK AS PER SPECIFICATIONS, DETAILS & DRAWINGS. COMPLETE IN ALL RESPECTS. | [13 empty] | 165-2-SPE-023 165-2-SPE-027
1.1 | SMALL WIRING FOR LIGHTS
1.1.1 | CIRCUIT WIRING FROM DISTRIBUTION BOARD (DB) TO SWITCH BOARD USING 3NOS OF 1C X 2.5 SQ.MM CU/PVC/PVC CABLE INCLUDING ANY WIRING BETWEEN DB TO SWITCH BOARD IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS. | 10 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.1.2 | WIRING FOR LIGHT POINT FROM SWITCH BOARD TO OTHER SWITCH BOARD USING 3NOS OF 1C X 2.5 SQ.MM PVC/PVC CABLE INCLUDING ANY WIRING BETWEEN SWITCH BOARD TO SWITCH BOARD IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS. | 9 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.1.3 | WIRING FOR LIGHT POINT FROM SWITCH BOARD TO FIRST LIGHT POINT USING 3C X 2.5 SQ.MM PVC/PVC CABLE INCLUDING ANY WIRING BETWEEN SWITCH BOARD TO LIGHT POINT IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS. | 35 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.1.4 | WIRING FOR LIGHT POINT FROM POINT TO POINT USING 3 nos of 1C X 1.5 SQ.MM PVC/PVC CABLE INCLUDING ANY WIRING BETWEEN LIGHT POINT TO LIGHT IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS. | 60 | NO.
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2 | SMALL WIRING FOR UTILITY POWER SOCKETS
1.2.1 | CIRCUIT WIRING FROM RESPECTIVE DISTRIBUTION BOARD (DB) TO 5A SWITCH SOCKET UNITS (FIRST OUTLET) USING FOLLOWING SIZE OF MUILTI CORE PVC INSULATED SOLID COPPER CONDUCTOR, COLOR CODED WIRES IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS.
1.2.1.1 | 3 NOS OF 1C - 2.5 SQMM AS PHASE, NEURAL & EARTH | 6 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.2 | WIRING FOR 5A SWITCH SOCKET UNITS FROM OUTLET TO OUTLET USING FOLLOWING SIZE OF SINGLE CORE PVC INSULATED SOLID COPPER CONDUCTOR, COLOR CODED WIRES IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS.
1.2.2.1 | 3 NOS OF 1C - 2.5 SQMM AS PHASE, NEURAL & EARTH | 12 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
1.2.3 | WIRING FOR 15A SWITCH SOCKET UNITS FROM DB TO OUTLET USING FOLLOWING SIZE OF SINGLE CORE PVC INSULATED SOLID COPPER CONDUCTOR, COLOR CODED WIRES IN 25 MM DIA PVC CONDUIT. COMPLETE WITH ALL ACCESSORIES AS SHOWN IN THE DRAWINGS.
1.2.3.1 | 3 NOS OF 1C - 4 SQMM AS PHASE, NEURAL & EARTH | 10 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
2 | WIRING DEVICES / RECEPTACLES
PROVIDING, INSTALLATION AND COMMISSIONING OF FOLLOWING WIRING DEVICES / LIGHT CONTROL SWITCHES / POWER RECEPTACLES AS PER BS STANDARDS INCLUDING 16 SWG MS POWDER COATED BACK BOXES, FLUSH WITH WALL AS SHOWN IN DRAWINGS AND DETAILS.
2.1 | LIGHT CONTROLLED SWITCHES
SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF 10A SWITCH, INDOOR (COMMERCIAL) TYPE, UV STABILIZED POLYCARBONATE FRONT PLATE COMPLETE WITH FLUSH MOUNTED BACK BOX AND INSTALLATION AND MOUNTING ACCESSORIES.
2.1.1 | 2-GANG SWITCH | 12 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
2.1.2 | 3-GANG SWITCH | 4 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
2.1.3 | 4-GANG SWITCH | 3 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
2.1.4 | 5-GANG SWITCH | 1 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
2.2 | UTILITY / CONDITIONED POWER RECEPTACLES
2.2.1 | 5A, SIMPLEX ROUND 2-PIN SWITCH SOCKET UNIT | 8 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
2.2.2 | 15A, SIMPLEX ROUND 3-PIN SWITCH SOCKET UNIT | 6 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3 | LIGHTING FIXTURES
3.1 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF 2X36W, 230V, FLUORESCENT LIGHT FIXTURE, SURFACE MOUNTED, WITH POLYCARBONATE DIFFUSER, CABLE ENTRIES FOR THROUGH (FIXTURE TO FIXTURE) WIRING, COMPLETE WITH ELECTRONIC BALLAST, CONTROL GEAR, LAMPS COMPLETE WITH ALL MOUNTING AND INSTALLATION ACCESSORIES. | 15 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.2 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF 4X18W, 230V, FLUORESCENT TROFFER LIGHT FIXTURE, RECESSED MOUNTED, WITH SPECULAR (M2 TYPE) LOUVERS, SHEET STEEL POWDER COATED WHITE BODY, PLASTIC END CAPS, CABLE ENTRIES FOR THROUGH (FIXTURE TO FIXTURE) WIRING, COMPLETE WITH ELECTRONIC BALLAST, CONTROL GEAR, LAMPS COMPLETE WITH ALL MOUNTING AND INSTALLATION ACCESSORIES. | 6 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.3 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF 1X10W, 230V, FLUORESCENT, SURFACE MOUNTED EXIT LIGHT, NON-MAINTAINED (WITH SELF-TEST FEATURE), WITH NIMH BATTERY BACKUP FOR 2 HOURS BACKUP OPERATION INJECTION MOLDED PLASTIC BODY, ACRYLIC DIFFUSER, 'EXIT' OR "EXIT+ARROW" SIGN, CABLE ENTRY, ELECTRONIC BALLAST, CONTROL GEAR, LAMP COMPLETE WITH ALL MOUNTING AND INSTALLATION ACCESSORIES. | 4 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
3.4 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF SURFACE MOUNTED DOWNLIGHT FIXTURE WITH 18W PLC LAMP ALL INSTALLATION AND MOUNTING ACCESSORIES. | 6 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
4 | FANS
| SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF 230V, 8 INCH SWEEP, EXHAUST FAN WITH SQUARE FRAME INCLUDING ALL MOUNTING AND INSTALLATION ACCESSORIES. | 2 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
5 | DISTRIBUTION PANELS / SWITCHBOARDS
SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF FOLLOWING DISTRIBUTION BOARDS IN ACCORDANCE WITH THE ATTACHED SINGLE LINE DIAGRAMS AND LAYOUT PLANS. THE PANELS SHALL BE MADE WITH 16 SWG SHEET STEEL HOUSING , POWDER COATED AFTER ANTIRUST PRIMERS. THE COPPER BUS BARS SHALL BE TIN ELECTROPLATED WITH PROTECTIVE COLOR CODED HEAT SHRINK SLEEVES. ALL DISTRIBUTION BOARDS SHALL FOR INDOOR INSTALLATIONS BUT PROVIDED WITH GAS KITS. ALL COMPONENTS AND ACCESSORIES SHALL BE AS PER THE SLD. CONTRACTOR HAS TO SUBMIT THE SHOP DRAWINGS PRIOR TO FABRICATION FOR CLIENT'S APPROVAL.
5.1 | LDB-CONTROL ROOM BUILDING (102-LDB-01) | 1 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELS-005
5.2 | LDB-MCCROOM & GEN SHED BUILDING (101-LDB-02) | 1 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-ELS-006
6 | CABLE RACEWAYS / CONTAINMENT
PROVIDING AND LAYING OF FOLLOWING PVC CONDUITS FOR MAIN / SUB MAIN CABLES, POWER , SECURITY AND COMMUNICATION RISERS FROM RESPECTIVE FLOORS TO PULL BOXES / PANELS AS SHOWN IN THE PLANS. COMPLETE WITH ALL ACCESSORIES LIKE JUNCTION BOXES, BENDS, SOCKETS , ELBOWS ETC. ALL ITEMS SHALL BE OF SAME MANUFACTURER.
6.1 | 25 MM DIA PVC CONDUIT. | 80 | RM. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7 | TELEPHONE & DATA CABLING
| PROVIDING , LAYING TESTING TAGGING COMISSIONING OF CATEGORY 6 , UTP CABLES, FOR TELEPHONE SYSTEM & DATA FROM SERVICE PROVIDER TO MAIN TJB OR DATA RACK AT BUILDING IN APPROPRIATE SIZE OF UNDER FLOOR PVC. WORK INCLUDES ALL TERMINATIONS, MANAGEMENT AND TAGGING AT BOTH ENDS. | 50 | RM. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-4-SPE-102
7.1 | 10 PAIR, 0.6 MM TELEPHONE CABLE FROM MAIN TJB TO OUTLET AT BUILDING IN APPROPRIATE SIZE OF PVC CONDUIT INCLUDING ALL ACCESSORIES. COMPLETE WITH TERMINATION AND TAGGING AT BOTH ENDS. | 30 | RM. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.2 | PATCH PANEL
| PATCH PANEL FOR DATA MAKE IN BUILDING INCLUDING WITH MARKING ARRANGEMENTS FOR 10 PAIR CABLES. | 2 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.3 | TELEPHONE JUNCTION BOX
| TELEPHONE JUNCTION BOX MAKE IN BUILDING INCLUDING WITH MARKING ARRANGEMENTS FOR 10 PAIR CABLES. | 1 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.4 | INFORMATION OUTLETS
7.4.1 | WORKSTATION/WALL/FLOOR OUTLET BOX MOUNTED INFORMATION OUTLET HAVING SIMPLEX FACE PLATE WITH 1NO. CAT-6, RJ-45 SOCKET FOR TELEPHONE SYSTEM INCLUDING SHUTTERED CLICK-INS, LABELS, JACKS ETC. COMPLETE IN ALL RESPECTS WITH CABLE IDENTIFICATION TAGS. | 6 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
7.4.2 | WORKSTATION/WALL/FLOOR OUTLET BOX MOUNTED INFORMATION OUTLET HAVING SIMPLEX FACE PLATE WITH 1NO. CAT-6, RJ-45 SOCKET FOR DATA COMMUNICATION SYSTEM INCLUDING SHUTTERED CLICK-INS, LABELS, JACKS ETC. COMPLETE IN ALL RESPECTS WITH CABLE IDENTIFICATION TAGS. | 8 | NO. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
8 | FIRE ALARM SYSTEM
| DESIGN, SUPPLY INSTALLATION, TESTING AND COMMISSIONING OF CONVENTIONAL ADDRESSABLE FIRE ALARM SYSTEM IN CIVIL CONSTRUCTED BUILDING OF PC TENDER SCOPE, COMPRISING OF FOLLOWING EQUIPMENTS INCLUDING ALL ACCESSORIES REQUIRED FOR THE COMPLETION OF THE SYSTEM COMPLETE IN ALL RESPECTS. FIRE / ALARM SYSTEM SHALL CONSIST OF BUT NOT LIMITED TO FOLLOWING MAJOR COMPONENTS | 1 | JOB. |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 165-2-SPE-022
SMOKE DETECTORS / HEAT DETECTORS / UV FLARE DETECTORS (SELECTION OF OPTIMUM TYPE OF DETECTOR SHALL BE CONTRACTOR RESPONSIBILITY). BREAK GLASS TYPE MANUAL CALL STATIONS BREAK GLASS SHALL ALSO INCORPORATES AN INDICATION LED FLESHED AFTER PRESSING THE BUTTON TO ACKNOWLEDGE THE ACTIVATION AND KEY OPERATION FACILITY FOR TESTING PURPOSES.
INDOOR ELECTRONIC SOUNDERS WITH FLASHER, MINIMUM SOUND OUTPUT 100 DB AT 1METER WITH FREQUENCIES FOR VARIETY OF SOUNDS AS REQUIRED.
ADDRESSABLE FIRE ALARM CONTROL PANEL(S) MINIMUM OF TWO LOOPS WITH ANY COMMUNICATION MODULES REQUIRED TO INTERFACE / INTEGRATE MULTIPLE FACPS. COMPLETE SYSTEM INTEGRATION, TESTING & COMMISSIONING OF THE SYSTEM INCLUDING ALL SOFTWARE / FIRMWARE / HARDWARE REQUIREMENTS, AS REQUIRED FOR SUCCESSFUL COMMISSIONING OF THE SYSTEM AS PER RELEVANT INTERNATIONAL STANDARDS AND INDUSTRY NARROWS.
COMPLETE SYSTEM WIRING / CABLING INCLUDING POWER CABLING, SIGNAL WIRING, ETC. COMPLETE WITH ALL REQUIRED CABLE WAYS (CONDUITS / TRAY, ETC). WIRING FOR COMPLETE FIRE ALARM SYSTEM USING 2C, 1.5 SQ. MM. LSZH CABLE IN APPROPRIATE SIZE OF GI CONDUITS. COMPLETE IN ALL RESPECTS. POWER WIRING FOR FACP FROM EMERGENCY DB IN USING 3 X 1.5 SQMM SINGLE CORE PVC INSULATED WIRES IN APPROPRIATE SIZE OF PVC CONDUIT. COMPLETE IN ALL RESPECTS.
| Total Price (1 to 8) | [7 empty] | 0 |  |  |  | 0 | 0
NOTES:
1 | All taxes shall be payable by contractor.
2 | The quantities mentioned in the BOQs are indicative and may change as detail design progresses. The bid evaluation will be carried out considering the quantities given in BOQs and unit rates quoted by the Bidders.
3 | Test certificates and MTC's of all items (where applicable) shall be provided.
4 | The charges shall be supported by verified quotation of Inspection Agency.

## Sheet1 (hidden)
1721125 | 2234 | 770.423
1175175 | 1433 | 820.0803
1545975 | 1840 | 840.2038
1256300 | 1850 | 679.0811
1680000 | 2400
#REF! | 2400 | #REF!