TENDER # PROC-LD/PT/P&P/17431/18 – PROTECTION RELAYS

|  | OIL & GAS DEVELOPMENT COMPANY LIMITED |  |  |
| --- | --- | --- | --- |
| Document |  | BOQ FOR SUPPLY OF DIGITAL MICROPROCESSOR BASED MULTIFUNCTION STATIC PROTECTION RELAYS FOR MOTORS AND TRANSFORMERS FOR DAKHNI GAS PROCESSING PLANT | Sheets |
| Document # | BOQ | Attachment | 17 |

TABLE OF CONTENTS

| S# | Description | Sheet No. |
| --- | --- | --- |
| 0 | System detail | SHEET - 5 |
| 1 | General | SHEET - 6 |
| 2 | Existing relays to be replaced. | SHEET – 7 |
| 3 | BOQ & Specs for new relays | SHEET – 8 |
| 4 | Scope of Services | SHEET - 9 |
| 5 | TOR | SHEET - 10 |
| 6 | Transformers DATA | SHEET – 11-12 |
| 7 | Motors DATA | SHEET - 13-17 |
| 8 | Single Line Diagram | Can be provided on demand |
| 9 | Schematics & Wiring Diagram of existing relays | Can be provided on demand |
| 10 | Switchboard & Relay Snapshots | Can be provided on demand |
| 11 | Existing Relay Catalogues | Can be provided on demand |

- SYSTEM DETAILS

The Electrical power systems at various utilization voltages are as follow:

Medium Voltages (MV)          6kV, 3 Phase, 3 Wire, 50Hz, resistance earthed

Low Voltage (LV)                   0.4kV, 3 phase, 4 Wire, 50Hz, neutral solidly earthed

       800A, 6kV medium voltage Bus bar

       Gas Turbines Generators               = 3 Nos. (5MW + 2.5 MW + 2.5MW)

       Distribution transformer feeders     = 4 Nos. (Including 1 Spare)

       MV motor feeders                           = 12 Nos.

Installed Relays:

|  | Generator Incomer Relays | = 3 x 7UM62 |
| --- | --- | --- |
|  | Motor Feeder Relays | = 3 x P225 + 8 x CTM42 + 1 x CTM41 |
|  | Transformer Feeder Relays | = 3 x CDG61 + 1 x P115 |

|  |  | S/No |  | Description |  | Specified | Offered |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | (To be filled by Vendor) |
| 1 |  |  |  | General |  |  |  |
|  |  |  | 1.1 | Application. |  | Motor & Transformer Feeder Protection |  |
|  |  |  |  |  |  | -This Document |  |
|  |  |  |  |  |  | - Single Line Diagram shall be provided on demand |  |
|  |  |  | 1.2 | Reference data. |  | - Schematics & Wiring Diagram shall be provided on demand |  |
|  |  |  |  |  |  | - Switchboard & Relay Snapshots shall be provided on demand |  |
|  |  |  |  |  |  | - Existing Relay Catalogues shall be provided on demand |  |
|  |  |  | 1.3 | Standards. |  | - IEC 60255 |  |
|  |  |  |  |  |  | - Applicable IEC/ANSI standards |  |
|  |  |  |  |  |  | - Factory test certificates. |  |
|  |  |  | 1.4 | Applicable Documents |  | - Schematics & Wiring Diagram |  |
|  |  |  |  |  |  | - FAT procedure documents |  |
|  |  |  |  |  |  | - All applicable as per standards. |  |
|  |  |  |  |  |  | - This BOQ with vendor response on all items individually. |  |
|  |  |  | 1.5 | Documentation required with quotation. |  | - Technical Data of the items offered. |  |
|  |  |  |  |  |  | - Price Schedule of each item & services offered as per SOR. |  |
|  |  |  |  |  |  | -As Built documents, hard and soft copies; catalogues; |  |
|  |  |  | 1.6 | Project Documentation. |  | Reports of inspections, tests, settings, commissioning. |  |
|  |  |  |  |  |  | Software shall be provided for system configuration. |  |
|  |  |  | 1.7 | Delivery Schedule |  | -As per SOR. |  |

BOQ: EXISTING RELAYS TO BE REPLACED WITH NEW DIGITAL RELAYS & SWITCHGEAR MODIFICATION

|  |  | S/No |  | Parameter |  |  |  |  | Specified | Offered |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | (To be filled by Vendor) |
| 2 |  |  |  | Bill of Quantity |  |  |  |  |  |  |
|  |  |  |  |  | Description | Rating | Current | Existing Relay |  |  |
|  |  |  | 2.1 | Air Cond. Package PA-501 CT Ratio: 50/5 Relay No: 045834W |  | 336KW | 39A | CTM 42 DF2AJ1452L |  |  |
|  |  |  | 2.2 | Air Blower(S.R.U) GA-701B CT Ratio: 50/5 Relay No: 045841W |  | 187KW | 23A | CTM 42 DF2AJ1452L |  |  |
|  |  |  | 2.3 | Air Blower(S.R.U) GB-701A CT Ratio: 30/5 Relay No: 045836W |  | 187KW | 23A | CTM 42 DF2AJ1452L |  |  |
|  |  |  | 2.4 | Lean Amine Pump GA-403-A CT Ratio: 100/5 Relay No: 045840W |  | 755KW | 89A | CTM 42 DF2AJ1452L |  |  |
|  |  |  | 2.5 | Lean Amine Pump GA-403-B CT Ratio: 100/5 Relay No: 045837W |  | 755KW | 89A | CTM 42 DF2AJ1452L | Digital Motor Protection Relays Qty = 9 |  |
|  |  |  | 2.6 | Hot Oil Pump 830-GA-01A CT Ratio: 30/5 Relay No: 045838W |  | 155KW | 22A | CTM 42 DF2AJ1452L | Digital Transformer Protection Relays Qty = 3 |  |
|  |  |  | 2.7 | Hot Oil Pump 830-GA-01B CT Ratio: 30/5 Relay No: 045839W |  | 155KW | 22A | CTM 42 DF2AJ1452L | [1 x CTM41 + 8 x CTM42 + 3 x CDG61 relays shall be |  |
|  |  |  |  |  |  |  |  |  | replaced] |  |
|  |  |  | 2.8 | Hot Oil Pump 830-GA-01C CT Ratio: 30/5 Relay No: 045839W |  | 155KW | 22A | CTM 42 DF2AJ1452L |  |  |
|  |  |  | 2.9 | Fire Water Pump 901-GA-01A CT Ratio: 30/5 Relay No: 045833W |  | 220KW | 27A | CTM 41 DF2AJ1452L |  |  |
|  |  |  | 2.10 | TRANSRORMER 1 CT Ratio 200/5 |  | 2000KVA | 192.45 | CDG 61/SPEC8FF98G |  |  |
|  |  |  | 2.11 | TRANSRORMER 2 CT Ratio 200/5 |  | 2000KVA | 192.45 | CDG 61/SPEC8FF98G |  |  |
|  |  |  | 2.12 | TRANSRORMER 4 CT Ratio 200/5 |  | 2000KVA | 192.45 | CDG 61/SPEC8FF98G |  |  |

BOQ: NEW DIGITAL RELAYS & SWITCHGEAR MODIFICATION

|  |  |  |  | S/No |  | Parameter |  | Specified | Offered |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | (To be filled by Vendor) |
| 3 |  |  |  |  |  | Technical |  |  |  |
|  | A |  |  |  |  | Motor Protection Relays: (Required quantity = 09 Nos.) |  | VTS = Vendor To Specify |  |
|  |  |  |  |  | 3.1 | Make |  | VTS |  |
|  |  |  |  |  | 3.2 | Model |  | VTS |  |
|  |  |  |  |  | 3.3 | Thermal (Th) Protection |  | Required |  |
|  |  |  |  |  | 3.4 | Instantaneous three phase overcurrent (I1) Protection |  | Required |  |
|  |  |  |  |  | 3.5 | Instantaneous unbalance & single phasing (I2) Protection |  | Required |  |
|  |  |  |  |  | 3.6 | Instantaneous earth fault (I0) Protection |  | Required |  |
|  |  |  |  |  | 3.7 | RTD Functionality |  | Required |  |
|  |  |  |  |  | 3.8 | No. of RTD Inputs |  | VTS as per existing schematics |  |
|  |  |  |  |  | 3.9 | Measurement Functionality (Voltage, Current) |  | Required |  |
|  |  |  |  |  | 3.10 | Communication protocol |  | Required |  |
|  |  |  |  |  | 3.11 | AC Current Inputs |  | Required |  |
|  |  |  |  |  | 3.12 | Power Supply |  | Control Supply= 110VDC ; Aux. Supply= 220/230VAC |  |
|  |  |  |  |  | 3.13 | Contacts |  | Required |  |
|  |  |  |  |  | 3.14 | Frequency |  | 50 Hz |  |
|  |  |  |  |  | 3.15 | Operating Temperature |  | Ambient 50 deg C |  |
|  | B |  |  |  |  | Transformer Protection: (Required quantity = 03 Nos.) |  |  |  |
|  |  |  |  |  | 3.16 | Make |  | VTS |  |
|  |  |  |  |  | 3.17 | Model |  | VTS |  |
|  |  |  |  |  | 3.18 | IDMT Overcurrent and Earth fault Protection |  | Required |  |
|  |  |  |  |  | 3.19 | Measurement Functionality (Voltage, Current) |  | Required |  |
|  |  |  |  |  | 3.20 | Communication protocol |  | Required |  |
|  |  |  |  |  | 3.21 | AC Current Inputs |  | Required |  |
|  |  |  |  |  | 3.22 | Power Supply |  | Control Supply= 110VDC ; Aux. Supply= 220/230VAC |  |
|  |  |  |  |  | 3.23 | Contacts |  | Required |  |
|  |  |  |  |  | 3.24 | Frequency |  | 50 Hz |  |
|  |  |  |  |  | 3.25 | Operating Temperature |  | Ambient 50 deg C |  |

SCOPE OF SERVICES FOR INSTALLATION, COMMISSIONING & TESTING OF NEW DIGITAL RELAYS AND SWITCHGEAR MODIFICATION

|  |  | S# |  | DESCRIPTION |  | Specified | Offered |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | (To be filled by Vendor) |
| 4 |  |  |  | Scope of Services |  |  |  |
|  |  |  |  | Modification works in the existing installed 6kV MV panel shall include but not limited to; |  |  |  |
|  |  |  |  | - Physical removal and handing over of installed relays to OGDCL site team. |  |  |  |
|  |  |  |  | - Installation of new digital relays. |  |  |  |
|  |  |  | 4.1 | - Supply of Control Supply (110VDC) & Aux. Supply (220/230VAC) from existing system to new relays. |  | Required |  |
|  |  |  |  | - Internal wiring, lugs, connectors, MCBs, power & control terminals, ferrules, nuts, bolts, lugs etc. |  |  |  |
|  |  |  |  | - Cutting/modifications in the panel door for the installation of new relays shall be complete in all respects. |  |  |  |
|  |  |  |  | - Site visit for assessment of panel existing metering and protection devices. |  |  |  |
|  |  |  |  | - It is the responsibility of the supplier/vendor/contractor to conduct a site visit and acquire data itself for replacement of |  |  |  |
|  |  |  |  | old relay and installation of new digital relays on the same cubical / panel door. All material will be arranged by the |  |  |  |
|  |  |  |  | Supplier / contractor. |  |  |  |
|  |  |  | 4.2 | Wiring diagrams for proposed digital protection relays |  | Required |  |
|  |  |  | 4.3 | Testing, Pre-Commissioning, Commissioning, Setting of parameters, Performance testing etc |  | Required |  |
|  |  |  | 4.4 | Warranties |  | Required |  |
|  |  |  | 4.5 | Factory or Site Acceptance Tests |  | Required |  |
|  |  |  | 4.6 | Onsite training of O & M team for digital protection relays |  | Required |  |
|  |  |  | 4.7 | As Built Documents and Software. |  | Required |  |

SUBJECT: TOR FOR THE SUPPLY OF DIGITAL MICROPROCESSOR BASED MULTIFUNCTION STATIC RELAYS FOR PROTECTION OF MOTORS AND TRANSFORMERS FOR DAKHNI GAS PROCESSING PLANT.

- The bidder shall be an OEM (Original Equipment Manufacturer). The quotation must include manufacturer name and country of origin.

- The relays shall be from reputable brands preferably American & European origin.

- The OEM shall have at least 10 years of successful working history in the Pakistani market.

- The bidder shall completely fill the response against each item mentioned in BOQ.

- The project shall be executed on fast track basis during the forthcoming annual turnaround of OGDCL Dakhni plant probably in the month of March, 2019.

- All existing protection, control & metering interfaces shall be retained.

- Relay coordination study shall be provided by OGDCL through its consultant which will include protection settings only.

- The Relay configuration/parameterization files shall be prepared and uploaded in the Relay by the vendor.

- It is the responsibility of the supplier / vendor to conduct a site visit and acquire/verify all the required data itself for replacement of relays in the same panel and therefore pre bid visit is mandatory.

- The supply cost should include the supply of relays and other related materials necessary for satisfactory installation of new digital relays alongwith  services for installation, commissioning and testing (up to  the level of satisfaction of OGDCL & Engineering consultant).

- The Supplier shall provide the installation, operation and maintenance manuals of the offered system.

- All wiring shall be properly dressed.

- Existing System: Control Supply= 110VDC ; Aux. Supply= 220/230VAC

- The Supplier shall specify the delivery period in its proposal.

- It is the responsibility of Supplier to transport the equipment safely at site.

- The successful bidder shall provide all the drawings & documents for approval to OGDCL/engineering consultant.

- The successful bidder shall provide wiring diagrams, component list, method statement, and cut-over plan etc., prior to start any work at the site.

- The contractor will provide 03 sets of as-built drawings to OGDCL/engineering consultant in addition to those supplied and shipped with the equipment in the document/material case.

- Licensed Software of digital protection relays will also be provided to OGDCL site team on the suitable device for future use.

- The supplier shall guarantee that equipment is free from fault and fulfill required / specified operating conditions. Should any defect in relay developed during guarantee period in operation, the supplier shall provide new relay in replacement of defective equipment/component at his own cost including transportation, testing and installation. Repaired equipment will not be accepted at all.